## Report Cover
Battery Capacity Test Report
Branch | MF
Batteries Name | SBS Substation
Battery Brand | STT
Battery Model | STT2V350
Battery ProducedTime | 2011-11-28
Battery FirstUsedTime | 2011-11-28
Nominal Capacity | 395
Monomer Voltage | 2
Discharge Rate | 7
Test Department
Test Time | 11/23/2011 9:03:32 AM

## First And Last Vol Data
| The beginning Voltage(V) | The Ending Voltage(V)
Standard Voltages(V) | 2.116 | 1.811
#1 | 2.113 | 1.781
#2 | 2.116 | 1.769
#3 | 2.11 | 1.781
#4 | 2.112 | 1.811
#5 | 2.111 | 1.796
#6 | 2.115 | 1.788

## Voltage Data Form1
Time(HMS) | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:01 | 0:01 | 0:01 | 0:01 | 0:01 | 0:01 | 0:01 | 0:01 | 0:01 | 0:02 | 0:02 | 0:02 | 0:02 | 0:02 | 0:02 | 0:02 | 0:02 | 0:02 | 0:02 | 0:02 | 0:03 | 0:03 | 0:03 | 0:03 | 0:03 | 0:04 | 0:05 | 0:06 | 0:07 | 0:08 | 0:09 | 0:10 | 0:11 | 0:12 | 0:13 | 0:14 | 0:15 | 0:16 | 0:17 | 0:18 | 0:19 | 0:20 | 0:21 | 0:22 | 0:23 | 0:24 | 0:25 | 0:26 | 0:27 | 0:28 | 0:29 | 0:30 | 0:31 | 0:32 | 0:33 | 0:34 | 0:35 | 0:36 | 0:37 | 0:38 | 0:39 | 0:40 | 0:41 | 0:42 | 0:43 | 0:44 | 0:45 | 0:46 | 0:47 | 0:48 | 0:49 | 0:50 | 0:51 | 0:52 | 0:53 | 0:54 | 0:55 | 0:56 | 0:57 | 0:58 | 0:59 | 1:00 | 1:01 | 1:02 | 1:03 | 1:04 | 1:05 | 1:06 | 1:07 | 1:08 | 1:09 | 1:10 | 1:11 | 1:12 | 1:13 | 1:14 | 1:15 | 1:16 | 1:17 | 1:18 | 1:19 | 1:20 | 1:21 | 1:22 | 1:23 | 1:24 | 1:25 | 1:26 | 1:27 | 1:28 | 1:29 | 1:30 | 1:31 | 1:32 | 1:33 | 1:34 | 1:35 | 1:36 | 1:37 | 1:38 | 1:39 | 1:40 | 1:41 | 1:42 | 1:43 | 1:44 | 1:45 | 1:46 | 1:47 | 1:48 | 1:49 | 1:50 | 1:51 | 1:52 | 1:53 | 1:54 | 1:55 | 1:56 | 1:57 | 1:58 | 1:59 | 2:00 | 2:01 | 2:02 | 2:03 | 2:04 | 2:05 | 2:06 | 2:07 | 2:08 | 2:09 | 2:10 | 2:11 | 2:12 | 2:13 | 2:14 | 2:15 | 2:16 | 2:17 | 2:18 | 2:19 | 2:20 | 2:21 | 2:22 | 2:23 | 2:24 | 2:25 | 2:26 | 2:27 | 2:28 | 2:29 | 2:30 | 2:31 | 2:32 | 2:33 | 2:34 | 2:35 | 2:36 | 2:37 | 2:38 | 2:39 | 2:40 | 2:41 | 2:42 | 2:43 | 2:44 | 2:45 | 2:46 | 2:47 | 2:48 | 2:49 | 2:50 | 2:51 | 2:52 | 2:53 | 2:54 | 2:55 | 2:56 | 2:57 | 2:58 | 2:59 | 3:00 | 3:01 | 3:02 | 3:03 | 3:04 | 3:05 | 3:06 | 3:07 | 3:08 | 3:09 | 3:10 | 3:11 | 3:12
Vol(V) | 12.6 | 12.6 | 12.4 | 12.1 | 12 | 11.9 | 11.8 | 11.8 | 11.8 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.8 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.6 | 11.7 | 11.7 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.6 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
Current(A) | 0 | -15 | -46.8 | -65.8 | -65.3 | -64.9 | -64.7 | -64.5 | -64.2 | -64.1 | -64.1 | -64.1 | -64.2 | -64.3 | -64.3 | -64.4 | -64.5 | -64.5 | -64.6 | -64.7 | -64.7 | -64.7 | -64.8 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -65 | -65 | -65 | -65.1 | -65.1 | -65.1 | -65.1 | -65.1 | -65.1 | -65.1 | -65 | -65 | -65 | -65 | -65 | -65 | -65 | -65 | -65 | -65 | -65 | -65 | -65 | -65 | -65 | -65 | -65 | -65 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.9 | -64.8 | -64.9 | -64.8 | -64.8 | -64.7 | -64.7 | -64.7 | -64.7 | -64.7 | -64.7 | -64.7 | -64.7 | -64.7 | -64.7 | -64.7 | -64.7 | -64.7 | -64.7 | -64.7 | -64.7 | -64.7 | -64.7 | -64.7 | -64.6 | -64.5 | -64.5 | -64.5 | -64.5 | -64.5 | -64.5 | -64.5 | -64.5 | -64.5 | -64.5 | -64.5 | -64.5 | -64.5 | -64.5 | -64.5 | -64.5 | -64.5 | -64.5 | -64.4 | -64.4 | -64.4 | -64.3 | -64.3 | -64.3 | -64.3 | -64.3 | -64.3 | -64.3 | -64.3 | -64.3 | -64.3 | -64.3 | -64.3 | -64.3 | -64.3 | -64.3 | -64.3 | -64.2 | -64.2 | -64.2 | -64.1 | -64.1 | -64.1 | -64.1 | -64.1 | -64.1 | -64.1 | -64.1 | -64.1 | -64.1 | -64.1 | -64.1 | -64.1 | -64.1 | -64.1 | -64.1 | -64.1 | -64.1 | -64 | -64 | -63.9 | -63.9 | -63.9 | -63.9 | -63.9 | -63.9 | -63.9 | -63.9 | -63.9 | -63.9 | -63.9 | -63.9 | -63.9 | -63.7 | -63.7 | -63.7 | -63.7 | -63.7 | -63.7 | -63.7 | -63.7 | -63.7 | -63.7 | -63.7 | -63.7 | -63.7 | -63.7 | -63.6 | -63.6 | -63.6 | -63.5 | -63.5 | -63.5 | -63.5 | -63.5 | -63.5 | -63.5 | -63.5 | -63.5 | -63.5 | -63.5 | -63.5 | -63.4 | -63.4 | -63.3 | -63.3 | -63.3 | -63.3 | -63.3 | -63.3 | -63.3 | -63.3 | -63.3 | -63.3 | -63.3 | -63.3 | -63.2 | -63.1 | -63.1
Cap(AH) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -3 | -4 | -5 | -6 | -7 | -8 | -9 | -10 | -11 | -12 | -13 | -15 | -16 | -17 | -18 | -19 | -20 | -21 | -22 | -23 | -24 | -25 | -26 | -28 | -29 | -30 | -31 | -32 | -33 | -34 | -35 | -36 | -37 | -38 | -39 | -40 | -42 | -43 | -44 | -45 | -46 | -47 | -48 | -49 | -50 | -51 | -52 | -53 | -55 | -56 | -57 | -58 | -59 | -60 | -61 | -62 | -63 | -64 | -65 | -66 | -68 | -69 | -70 | -71 | -72 | -73 | -74 | -75 | -76 | -77 | -78 | -79 | -80 | -82 | -83 | -84 | -85 | -86 | -87 | -88 | -89 | -90 | -91 | -92 | -93 | -94 | -95 | -97 | -98 | -99 | -100 | -101 | -102 | -103 | -104 | -105 | -106 | -107 | -108 | -109 | -111 | -112 | -113 | -114 | -115 | -116 | -117 | -118 | -119 | -120 | -121 | -122 | -123 | -124 | -125 | -127 | -128 | -129 | -130 | -131 | -132 | -133 | -134 | -135 | -136 | -137 | -138 | -139 | -140 | -142 | -143 | -144 | -145 | -146 | -147 | -148 | -149 | -150 | -151 | -152 | -153 | -154 | -155 | -156 | -157 | -159 | -160 | -161 | -162 | -163 | -164 | -165 | -166 | -167 | -168 | -169 | -170 | -171 | -172 | -173 | -174 | -176 | -177 | -178 | -179 | -180 | -181 | -182 | -183 | -184 | -185 | -186 | -187 | -188 | -189 | -190 | -191 | -192 | -194 | -195 | -196 | -197 | -198 | -199 | -200 | -201 | -202 | -203 | -204 | -205
STD Vol(V) | 2.116 | 2.109 | 2.076 | 2.031 | 2.013 | 1.998 | 1.986 | 1.98 | 1.974 | 1.968 | 1.967 | 1.967 | 1.967 | 1.967 | 1.97 | 1.973 | 1.973 | 1.973 | 1.976 | 1.976 | 1.976 | 1.977 | 1.979 | 1.979 | 1.979 | 1.979 | 1.982 | 1.982 | 1.982 | 1.982 | 1.982 | 1.985 | 1.986 | 1.986 | 1.986 | 1.986 | 1.986 | 1.986 | 1.986 | 1.986 | 1.986 | 1.986 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.976 | 1.976 | 1.976 | 1.977 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.971 | 1.974 | 1.974 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.969 | 1.972 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.966 | 1.966 | 1.966 | 1.966 | 1.966 | 1.966 | 1.966 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.957 | 1.957 | 1.957 | 1.957 | 1.957 | 1.957 | 1.957 | 1.957 | 1.954 | 1.954 | 1.954 | 1.954 | 1.954 | 1.954 | 1.954 | 1.954 | 1.954 | 1.951 | 1.951 | 1.951 | 1.951 | 1.951 | 1.951 | 1.948 | 1.948 | 1.948 | 1.949 | 1.948 | 1.948 | 1.948 | 1.948 | 1.948 | 1.948 | 1.948 | 1.948 | 1.944 | 1.945 | 1.945 | 1.945 | 1.945 | 1.943 | 1.943 | 1.943 | 1.943 | 1.942 | 1.942 | 1.942 | 1.942 | 1.942 | 1.94 | 1.94 | 1.94 | 1.94 | 1.939 | 1.939 | 1.939 | 1.936 | 1.936 | 1.936 | 1.936 | 1.936 | 1.936 | 1.936 | 1.936 | 1.936 | 1.933 | 1.933 | 1.933 | 1.933 | 1.933 | 1.933 | 1.933 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.927 | 1.927 | 1.93 | 1.927 | 1.927 | 1.927 | 1.927 | 1.927 | 1.924 | 1.924 | 1.924
#1 | 2.113 | 2.099 | 2.063 | 2.013 | 1.993 | 1.981 | 1.971 | 1.965 | 1.962 | 1.962 | 1.962 | 1.965 | 1.965 | 1.965 | 1.968 | 1.968 | 1.971 | 1.971 | 1.974 | 1.974 | 1.974 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.98 | 1.98 | 1.977 | 1.977 | 1.977 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.977 | 1.977 | 1.977 | 1.974 | 1.974 | 1.974 | 1.974 | 1.971 | 1.971 | 1.971 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.971 | 1.974 | 1.971 | 1.974 | 1.974 | 1.974 | 1.974 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.968 | 1.968 | 1.971 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.965 | 1.968 | 1.968 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.962 | 1.962 | 1.962 | 1.963 | 1.963 | 1.963 | 1.963 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.957 | 1.957 | 1.957 | 1.957 | 1.957 | 1.957 | 1.957 | 1.954 | 1.957 | 1.957 | 1.954 | 1.954 | 1.954 | 1.954 | 1.954 | 1.954 | 1.954 | 1.951 | 1.954 | 1.954 | 1.951 | 1.951 | 1.951 | 1.951 | 1.951 | 1.951 | 1.948 | 1.949 | 1.949 | 1.949 | 1.946 | 1.946 | 1.946 | 1.949 | 1.946 | 1.946 | 1.946 | 1.946 | 1.946 | 1.943 | 1.943 | 1.943 | 1.943 | 1.943 | 1.943 | 1.943 | 1.943 | 1.943 | 1.943 | 1.943 | 1.943 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.939 | 1.936 | 1.936 | 1.936 | 1.936 | 1.936 | 1.936 | 1.933 | 1.933 | 1.933 | 1.933 | 1.933 | 1.933 | 1.933 | 1.93 | 1.933 | 1.933 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.927 | 1.927 | 1.927 | 1.927 | 1.927 | 1.927 | 1.927 | 1.927 | 1.924 | 1.924 | 1.924
#2 | 2.116 | 2.103 | 2.065 | 2.019 | 2 | 1.985 | 1.979 | 1.97 | 1.967 | 1.967 | 1.967 | 1.967 | 1.967 | 1.967 | 1.97 | 1.973 | 1.973 | 1.973 | 1.976 | 1.976 | 1.976 | 1.976 | 1.979 | 1.979 | 1.979 | 1.979 | 1.982 | 1.982 | 1.982 | 1.982 | 1.982 | 1.985 | 1.985 | 1.985 | 1.985 | 1.982 | 1.982 | 1.982 | 1.982 | 1.982 | 1.979 | 1.979 | 1.982 | 1.979 | 1.979 | 1.979 | 1.979 | 1.979 | 1.976 | 1.976 | 1.976 | 1.976 | 1.976 | 1.976 | 1.976 | 1.976 | 1.976 | 1.976 | 1.976 | 1.976 | 1.976 | 1.976 | 1.976 | 1.976 | 1.976 | 1.977 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.971 | 1.974 | 1.974 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.969 | 1.972 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.969 | 1.966 | 1.966 | 1.966 | 1.966 | 1.966 | 1.966 | 1.966 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.963 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.957 | 1.957 | 1.957 | 1.957 | 1.957 | 1.957 | 1.957 | 1.957 | 1.954 | 1.954 | 1.954 | 1.954 | 1.954 | 1.954 | 1.954 | 1.954 | 1.954 | 1.951 | 1.951 | 1.951 | 1.951 | 1.951 | 1.951 | 1.948 | 1.948 | 1.948 | 1.948 | 1.948 | 1.948 | 1.948 | 1.948 | 1.948 | 1.948 | 1.948 | 1.948 | 1.944 | 1.945 | 1.945 | 1.945 | 1.945 | 1.942 | 1.942 | 1.942 | 1.942 | 1.942 | 1.942 | 1.942 | 1.942 | 1.942 | 1.939 | 1.939 | 1.939 | 1.939 | 1.939 | 1.939 | 1.939 | 1.936 | 1.936 | 1.936 | 1.936 | 1.936 | 1.936 | 1.936 | 1.936 | 1.936 | 1.933 | 1.933 | 1.933 | 1.933 | 1.933 | 1.933 | 1.933 | 1.93 | 1.93 | 1.93 | 1.93 | 1.93 | 1.927 | 1.927 | 1.93 | 1.927 | 1.926 | 1.926 | 1.926 | 1.923 | 1.923 | 1.923 | 1.923
#3 | 2.11 | 2.098 | 2.062 | 2.02 | 2.005 | 1.99 | 1.981 | 1.975 | 1.969 | 1.963 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.96 | 1.963 | 1.963 | 1.966 | 1.969 | 1.969 | 1.972 | 1.972 | 1.972 | 1.972 | 1.972 | 1.975 | 1.975 | 1.975 | 1.975 | 1.978 | 1.978 | 1.978 | 1.981 | 1.981 | 1.981 | 1.981 | 1.981 | 1.978 | 1.978 | 1.978 | 1.978 | 1.978 | 1.978 | 1.978 | 1.975 | 1.975 | 1.975 | 1.975 | 1.975 | 1.972 | 1.972 | 1.974 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.961 | 1.96 | 1.961 | 1.958 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.956 | 1.956 | 1.959 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.947 | 1.947 | 1.947 | 1.947 | 1.947 | 1.947 | 1.947 | 1.947 | 1.947 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.941 | 1.941 | 1.941 | 1.938 | 1.938 | 1.938 | 1.938 | 1.938 | 1.938 | 1.938 | 1.938 | 1.938 | 1.935 | 1.935 | 1.935 | 1.935 | 1.935 | 1.932 | 1.932 | 1.932 | 1.932 | 1.932 | 1.935 | 1.932 | 1.932 | 1.932 | 1.932 | 1.932 | 1.932 | 1.932 | 1.929 | 1.929 | 1.929 | 1.929 | 1.929 | 1.929 | 1.926 | 1.929 | 1.926 | 1.926 | 1.926 | 1.926 | 1.926 | 1.926 | 1.923 | 1.923 | 1.923 | 1.923 | 1.923 | 1.923 | 1.923 | 1.923 | 1.92 | 1.92 | 1.923 | 1.92 | 1.92 | 1.92 | 1.92 | 1.92 | 1.917
#4 | 2.112 | 2.096 | 2.06 | 2.022 | 2.002 | 1.99 | 1.981 | 1.972 | 1.969 | 1.966 | 1.963 | 1.959 | 1.959 | 1.959 | 1.959 | 1.962 | 1.962 | 1.965 | 1.968 | 1.968 | 1.971 | 1.971 | 1.971 | 1.974 | 1.974 | 1.974 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.98 | 1.98 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.947 | 1.947 | 1.947 | 1.947 | 1.947 | 1.947 | 1.947 | 1.947 | 1.947 | 1.947 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.941 | 1.941 | 1.941 | 1.941 | 1.941 | 1.941 | 1.941 | 1.941 | 1.941 | 1.938 | 1.938 | 1.938 | 1.938 | 1.938 | 1.938 | 1.938 | 1.935 | 1.935 | 1.935 | 1.935 | 1.935 | 1.935 | 1.935 | 1.935 | 1.935 | 1.935 | 1.935 | 1.932 | 1.932 | 1.932 | 1.932 | 1.932 | 1.932 | 1.932 | 1.932 | 1.932 | 1.929 | 1.929 | 1.929 | 1.929 | 1.929 | 1.929 | 1.926 | 1.926 | 1.926 | 1.926 | 1.926 | 1.926 | 1.926 | 1.926 | 1.926 | 1.923 | 1.923 | 1.923
#5 | 2.111 | 2.105 | 2.075 | 2.029 | 2.008 | 1.992 | 1.983 | 1.977 | 1.971 | 1.965 | 1.962 | 1.959 | 1.959 | 1.959 | 1.959 | 1.962 | 1.965 | 1.965 | 1.968 | 1.968 | 1.971 | 1.971 | 1.974 | 1.974 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.98 | 1.98 | 1.983 | 1.983 | 1.983 | 1.98 | 1.983 | 1.983 | 1.983 | 1.983 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.974 | 1.974 | 1.974 | 1.974 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.953 | 1.955 | 1.955 | 1.952 | 1.952 | 1.952 | 1.952 | 1.955 | 1.955 | 1.955 | 1.955 | 1.952 | 1.952 | 1.952 | 1.952 | 1.952 | 1.952 | 1.952 | 1.949 | 1.949 | 1.949 | 1.949 | 1.949 | 1.949 | 1.949 | 1.949 | 1.949 | 1.946 | 1.946 | 1.949 | 1.949 | 1.946 | 1.946 | 1.946 | 1.946 | 1.946 | 1.946 | 1.943 | 1.943 | 1.943 | 1.946 | 1.943 | 1.943 | 1.943 | 1.943 | 1.943 | 1.943 | 1.943 | 1.943 | 1.943 | 1.943 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.937 | 1.937 | 1.937 | 1.937 | 1.937 | 1.937 | 1.937 | 1.934 | 1.937 | 1.934 | 1.934 | 1.934 | 1.934 | 1.934 | 1.934 | 1.934 | 1.931 | 1.931 | 1.931 | 1.931 | 1.931 | 1.928 | 1.928 | 1.928 | 1.928 | 1.928 | 1.928 | 1.928 | 1.928 | 1.925 | 1.925 | 1.925 | 1.925 | 1.925 | 1.925 | 1.925 | 1.922 | 1.922 | 1.922 | 1.922 | 1.922 | 1.922 | 1.922 | 1.922
#6 | 2.115 | 2.109 | 2.076 | 2.031 | 2.013 | 1.998 | 1.986 | 1.98 | 1.974 | 1.968 | 1.965 | 1.965 | 1.965 | 1.962 | 1.962 | 1.965 | 1.965 | 1.968 | 1.968 | 1.971 | 1.971 | 1.974 | 1.974 | 1.977 | 1.977 | 1.977 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.983 | 1.986 | 1.986 | 1.986 | 1.986 | 1.986 | 1.986 | 1.986 | 1.986 | 1.986 | 1.986 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983 | 1.983 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.977 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.974 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.971 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.968 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.965 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.962 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.959 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.956 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.953 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.95 | 1.947 | 1.947 | 1.947 | 1.947 | 1.947 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.944 | 1.941 | 1.941 | 1.941 | 1.941 | 1.941 | 1.941 | 1.941 | 1.941 | 1.941 | 1.941 | 1.938 | 1.938 | 1.938 | 1.938 | 1.938 | 1.938 | 1.938 | 1.938 | 1.935 | 1.935 | 1.935 | 1.935 | 1.935 | 1.935 | 1.935 | 1.932 | 1.932 | 1.932 | 1.932 | 1.932 | 1.932 | 1.932 | 1.932 | 1.932 | 1.932 | 1.929 | 1.929 | 1.929 | 1.929 | 1.929 | 1.929 | 1.929 | 1.926 | 1.926 | 1.926 | 1.926 | 1.926 | 1.926 | 1.926 | 1.923 | 1.923 | 1.923 | 1.923 | 1.923 | 1.923 | 1.923

## Voltage Data Form2
3:13 | 3:14 | 3:15 | 3:16 | 3:17 | 3:18 | 3:19 | 3:20 | 3:21 | 3:22 | 3:23 | 3:24 | 3:25 | 3:26 | 3:27 | 3:28 | 3:29 | 3:30 | 3:31 | 3:32 | 3:33 | 3:34 | 3:35 | 3:36 | 3:37 | 3:38 | 3:39 | 3:40 | 3:41 | 3:42 | 3:43 | 3:44 | 3:45 | 3:46 | 3:47 | 3:48 | 3:49 | 3:50 | 3:51 | 3:52 | 3:53 | 3:54 | 3:55 | 3:56 | 3:57 | 3:58 | 3:59 | 4:00 | 4:01 | 4:02 | 4:03 | 4:04 | 4:05 | 4:06 | 4:07 | 4:08 | 4:09 | 4:10 | 4:11 | 4:12 | 4:13 | 4:14 | 4:15 | 4:16 | 4:17 | 4:18 | 4:19 | 4:20 | 4:21 | 4:22 | 4:23 | 4:24 | 4:25 | 4:26 | 4:27 | 4:28 | 4:29 | 4:30 | 4:31 | 4:32 | 4:33 | 4:34 | 4:35 | 4:36 | 4:37 | 4:38 | 4:39 | 4:40 | 4:41 | 4:42 | 4:43 | 4:44 | 4:45 | 4:46 | 4:47 | 4:48 | 4:49 | 4:50 | 4:51 | 4:52 | 4:53 | 4:54 | 4:55 | 4:56 | 4:57 | 4:58 | 4:59 | 5:00 | 5:01 | 5:02 | 5:03 | 5:04 | 5:05 | 5:06 | 5:07 | 5:08 | 5:09 | 5:10 | 5:11 | 5:12 | 5:13 | 5:14 | 5:15 | 5:16 | 5:17 | 5:18 | 5:19 | 5:20 | 5:21 | 5:22 | 5:23 | 5:24 | 5:25 | 5:26 | 5:27 | 5:28 | 5:29 | 5:30 | 5:31 | 5:32 | 5:33 | 5:34 | 5:35 | 5:36 | 5:37 | 5:38 | 5:39 | 5:40 | 5:41 | 5:42 | 5:43 | 5:44 | 5:45 | 5:46 | 5:47 | 5:48 | 5:49 | 5:50 | 5:51 | 5:52 | 5:53 | 5:54 | 5:55 | 5:56 | 5:57 | 5:58 | 5:59 | 6:00 | 6:01 | 6:02 | 6:03 | 6:04 | 6:05 | 6:06 | 6:07 | 6:08 | 6:09 | 6:10 | 6:11 | 6:12 | 6:13 | 6:14 | 6:15 | 6:16 | 6:17 | 6:17
11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.2 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7
-63.1 | -63.1 | -63.1 | -63.1 | -63.1 | -63.1 | -63.1 | -63.1 | -63.1 | -63 | -63 | -62.9 | -62.9 | -62.9 | -62.9 | -62.9 | -62.9 | -62.9 | -62.9 | -62.9 | -62.9 | -62.9 | -62.8 | -62.7 | -62.7 | -62.7 | -62.7 | -62.7 | -62.7 | -62.7 | -62.7 | -62.7 | -62.7 | -62.7 | -62.6 | -62.6 | -62.6 | -62.6 | -62.6 | -62.6 | -62.6 | -62.6 | -62.6 | -62.6 | -62.6 | -62.5 | -62.5 | -62.4 | -62.4 | -62.4 | -62.4 | -62.4 | -62.4 | -62.4 | -62.4 | -62.4 | -62.2 | -62.2 | -62.1 | -62.1 | -62.1 | -62.1 | -62.1 | -62.1 | -62.1 | -62.1 | -62 | -61.9 | -61.9 | -61.9 | -61.9 | -61.9 | -61.9 | -61.9 | -61.9 | -61.9 | -61.8 | -61.7 | -61.7 | -61.7 | -61.7 | -61.7 | -61.7 | -61.7 | -61.7 | -61.6 | -61.5 | -61.5 | -61.5 | -61.5 | -61.5 | -61.5 | -61.5 | -61.5 | -61.4 | -61.4 | -61.4 | -61.4 | -61.4 | -61.4 | -61.4 | -61.3 | -61.3 | -61.2 | -61.2 | -61.2 | -61.2 | -61.2 | -61.2 | -61.1 | -61.1 | -61 | -61 | -61 | -61 | -61 | -61 | -61 | -60.9 | -60.7 | -60.7 | -60.7 | -60.7 | -60.7 | -60.7 | -60.6 | -60.5 | -60.5 | -60.5 | -60.5 | -60.5 | -60.5 | -60.4 | -60.3 | -60.3 | -60.3 | -60.3 | -60.3 | -60.2 | -60.2 | -60.2 | -60.2 | -60.2 | -60.2 | -60.2 | -60.1 | -60 | -60 | -60 | -60 | -60 | -59.8 | -59.8 | -59.8 | -59.8 | -59.8 | -59.7 | -59.6 | -59.6 | -59.6 | -59.6 | -59.5 | -59.4 | -59.4 | -59.4 | -59.4 | -59.2 | -59.1 | -59.1 | -59.1 | -59.1 | -59 | -59 | -59 | -59 | -58.9 | -58.8 | -58.8 | -58.8 | -58.7 | -58.6 | -58.6 | -58.6 | -58.4 | -58.4 | -58.4
-206 | -207 | -208 | -209 | -210 | -211 | -212 | -214 | -215 | -216 | -217 | -218 | -219 | -220 | -221 | -222 | -223 | -224 | -225 | -226 | -227 | -228 | -229 | -230 | -231 | -232 | -233 | -234 | -236 | -237 | -238 | -239 | -240 | -241 | -242 | -243 | -244 | -245 | -246 | -247 | -248 | -249 | -250 | -251 | -252 | -253 | -254 | -255 | -256 | -257 | -258 | -260 | -261 | -262 | -263 | -264 | -265 | -266 | -267 | -268 | -269 | -270 | -271 | -272 | -273 | -274 | -275 | -276 | -277 | -278 | -279 | -280 | -281 | -282 | -283 | -284 | -285 | -286 | -287 | -288 | -289 | -291 | -292 | -293 | -294 | -295 | -296 | -297 | -298 | -299 | -300 | -301 | -302 | -303 | -304 | -305 | -306 | -307 | -308 | -309 | -310 | -311 | -312 | -313 | -314 | -315 | -316 | -317 | -318 | -319 | -320 | -321 | -322 | -323 | -324 | -325 | -326 | -327 | -328 | -329 | -330 | -331 | -332 | -333 | -334 | -335 | -336 | -337 | -338 | -339 | -340 | -341 | -342 | -343 | -344 | -345 | -346 | -347 | -349 | -350 | -351 | -352 | -353 | -354 | -355 | -356 | -357 | -358 | -359 | -360 | -361 | -362 | -363 | -364 | -365 | -366 | -367 | -367 | -368 | -369 | -370 | -371 | -372 | -373 | -374 | -375 | -376 | -377 | -378 | -379 | -380 | -381 | -382 | -383 | -384 | -385 | -386 | -387 | -388 | -389 | -390 | -391 | -392 | -393 | -394 | -395
1.924 | 1.923 | 1.923 | 1.923 | 1.923 | 1.921 | 1.921 | 1.921 | 1.921 | 1.92 | 1.92 | 1.92 | 1.92 | 1.918 | 1.918 | 1.918 | 1.917 | 1.917 | 1.917 | 1.915 | 1.915 | 1.915 | 1.914 | 1.914 | 1.914 | 1.914 | 1.914 | 1.914 | 1.911 | 1.911 | 1.911 | 1.911 | 1.911 | 1.911 | 1.908 | 1.908 | 1.908 | 1.908 | 1.906 | 1.906 | 1.905 | 1.905 | 1.905 | 1.905 | 1.905 | 1.903 | 1.902 | 1.902 | 1.902 | 1.902 | 1.902 | 1.902 | 1.899 | 1.899 | 1.899 | 1.899 | 1.899 | 1.899 | 1.896 | 1.896 | 1.896 | 1.896 | 1.896 | 1.893 | 1.893 | 1.893 | 1.893 | 1.893 | 1.893 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.887 | 1.887 | 1.887 | 1.887 | 1.887 | 1.884 | 1.884 | 1.884 | 1.884 | 1.884 | 1.884 | 1.881 | 1.881 | 1.881 | 1.881 | 1.881 | 1.881 | 1.878 | 1.878 | 1.878 | 1.878 | 1.878 | 1.875 | 1.875 | 1.875 | 1.875 | 1.875 | 1.872 | 1.872 | 1.872 | 1.872 | 1.872 | 1.869 | 1.869 | 1.869 | 1.869 | 1.869 | 1.869 | 1.866 | 1.866 | 1.866 | 1.866 | 1.866 | 1.863 | 1.863 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.857 | 1.853 | 1.853 | 1.853 | 1.853 | 1.853 | 1.85 | 1.85 | 1.85 | 1.85 | 1.85 | 1.847 | 1.847 | 1.847 | 1.844 | 1.844 | 1.844 | 1.844 | 1.844 | 1.841 | 1.841 | 1.841 | 1.841 | 1.838 | 1.838 | 1.838 | 1.838 | 1.835 | 1.835 | 1.835 | 1.835 | 1.832 | 1.832 | 1.832 | 1.829 | 1.829 | 1.829 | 1.826 | 1.826 | 1.826 | 1.826 | 1.823 | 1.823 | 1.823 | 1.82 | 1.82 | 1.82 | 1.817 | 1.817 | 1.817 | 1.817 | 1.814 | 1.814 | 1.814 | 1.811
1.924 | 1.921 | 1.921 | 1.921 | 1.921 | 1.921 | 1.921 | 1.921 | 1.921 | 1.918 | 1.918 | 1.918 | 1.918 | 1.918 | 1.918 | 1.918 | 1.915 | 1.915 | 1.915 | 1.915 | 1.915 | 1.915 | 1.912 | 1.912 | 1.912 | 1.912 | 1.912 | 1.909 | 1.909 | 1.909 | 1.909 | 1.909 | 1.909 | 1.909 | 1.906 | 1.906 | 1.906 | 1.906 | 1.906 | 1.906 | 1.903 | 1.903 | 1.903 | 1.903 | 1.903 | 1.903 | 1.9 | 1.9 | 1.9 | 1.9 | 1.897 | 1.897 | 1.897 | 1.897 | 1.897 | 1.894 | 1.894 | 1.894 | 1.894 | 1.894 | 1.894 | 1.891 | 1.891 | 1.891 | 1.891 | 1.891 | 1.891 | 1.891 | 1.891 | 1.888 | 1.888 | 1.888 | 1.885 | 1.885 | 1.885 | 1.885 | 1.885 | 1.882 | 1.882 | 1.882 | 1.882 | 1.879 | 1.879 | 1.879 | 1.879 | 1.879 | 1.876 | 1.879 | 1.876 | 1.876 | 1.876 | 1.873 | 1.873 | 1.87 | 1.873 | 1.873 | 1.873 | 1.87 | 1.87 | 1.869 | 1.869 | 1.866 | 1.869 | 1.866 | 1.866 | 1.866 | 1.863 | 1.863 | 1.863 | 1.86 | 1.86 | 1.86 | 1.86 | 1.857 | 1.857 | 1.854 | 1.857 | 1.857 | 1.857 | 1.854 | 1.854 | 1.853 | 1.853 | 1.853 | 1.85 | 1.85 | 1.848 | 1.848 | 1.848 | 1.845 | 1.845 | 1.845 | 1.845 | 1.842 | 1.842 | 1.842 | 1.839 | 1.839 | 1.839 | 1.839 | 1.835 | 1.835 | 1.832 | 1.835 | 1.835 | 1.832 | 1.832 | 1.829 | 1.829 | 1.829 | 1.826 | 1.826 | 1.826 | 1.822 | 1.822 | 1.822 | 1.819 | 1.819 | 1.816 | 1.816 | 1.816 | 1.816 | 1.813 | 1.813 | 1.81 | 1.81 | 1.807 | 1.807 | 1.804 | 1.804 | 1.804 | 1.801 | 1.801 | 1.798 | 1.799 | 1.796 | 1.796 | 1.794 | 1.791 | 1.791 | 1.788 | 1.788 | 1.784 | 1.781 | 1.781 | 1.781
1.923 | 1.923 | 1.923 | 1.923 | 1.923 | 1.92 | 1.92 | 1.92 | 1.92 | 1.92 | 1.92 | 1.92 | 1.917 | 1.917 | 1.917 | 1.917 | 1.917 | 1.917 | 1.917 | 1.914 | 1.914 | 1.914 | 1.911 | 1.911 | 1.911 | 1.911 | 1.911 | 1.911 | 1.911 | 1.911 | 1.908 | 1.908 | 1.908 | 1.908 | 1.908 | 1.905 | 1.905 | 1.905 | 1.905 | 1.905 | 1.905 | 1.902 | 1.902 | 1.902 | 1.902 | 1.902 | 1.899 | 1.899 | 1.899 | 1.899 | 1.896 | 1.899 | 1.896 | 1.896 | 1.896 | 1.896 | 1.896 | 1.893 | 1.893 | 1.893 | 1.893 | 1.893 | 1.893 | 1.893 | 1.89 | 1.89 | 1.89 | 1.887 | 1.887 | 1.887 | 1.887 | 1.887 | 1.884 | 1.884 | 1.884 | 1.884 | 1.881 | 1.881 | 1.881 | 1.881 | 1.881 | 1.881 | 1.878 | 1.878 | 1.878 | 1.878 | 1.875 | 1.875 | 1.875 | 1.875 | 1.872 | 1.872 | 1.872 | 1.872 | 1.869 | 1.868 | 1.868 | 1.868 | 1.868 | 1.868 | 1.868 | 1.865 | 1.865 | 1.865 | 1.862 | 1.862 | 1.865 | 1.862 | 1.862 | 1.859 | 1.859 | 1.856 | 1.859 | 1.856 | 1.856 | 1.853 | 1.853 | 1.853 | 1.853 | 1.853 | 1.849 | 1.849 | 1.849 | 1.846 | 1.846 | 1.846 | 1.843 | 1.843 | 1.843 | 1.843 | 1.843 | 1.84 | 1.84 | 1.84 | 1.84 | 1.837 | 1.837 | 1.834 | 1.833 | 1.833 | 1.833 | 1.833 | 1.832 | 1.829 | 1.826 | 1.826 | 1.826 | 1.823 | 1.823 | 1.823 | 1.82 | 1.82 | 1.82 | 1.817 | 1.817 | 1.817 | 1.814 | 1.814 | 1.814 | 1.811 | 1.808 | 1.808 | 1.805 | 1.805 | 1.805 | 1.805 | 1.802 | 1.799 | 1.796 | 1.796 | 1.796 | 1.793 | 1.793 | 1.79 | 1.787 | 1.787 | 1.784 | 1.784 | 1.781 | 1.781 | 1.778 | 1.778 | 1.775 | 1.772 | 1.772 | 1.769
1.917 | 1.917 | 1.917 | 1.917 | 1.917 | 1.914 | 1.914 | 1.914 | 1.914 | 1.914 | 1.914 | 1.914 | 1.911 | 1.911 | 1.911 | 1.911 | 1.911 | 1.911 | 1.911 | 1.908 | 1.908 | 1.908 | 1.908 | 1.908 | 1.908 | 1.908 | 1.905 | 1.905 | 1.905 | 1.905 | 1.905 | 1.902 | 1.902 | 1.902 | 1.902 | 1.902 | 1.902 | 1.902 | 1.902 | 1.902 | 1.902 | 1.899 | 1.899 | 1.899 | 1.899 | 1.899 | 1.899 | 1.896 | 1.896 | 1.896 | 1.896 | 1.896 | 1.893 | 1.893 | 1.893 | 1.893 | 1.893 | 1.891 | 1.891 | 1.891 | 1.888 | 1.891 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.885 | 1.885 | 1.885 | 1.885 | 1.882 | 1.882 | 1.882 | 1.882 | 1.882 | 1.879 | 1.879 | 1.879 | 1.879 | 1.879 | 1.876 | 1.876 | 1.876 | 1.876 | 1.876 | 1.876 | 1.873 | 1.876 | 1.873 | 1.873 | 1.873 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.867 | 1.867 | 1.867 | 1.864 | 1.864 | 1.864 | 1.864 | 1.864 | 1.861 | 1.861 | 1.861 | 1.861 | 1.858 | 1.858 | 1.858 | 1.855 | 1.855 | 1.858 | 1.858 | 1.855 | 1.852 | 1.852 | 1.855 | 1.852 | 1.852 | 1.852 | 1.849 | 1.849 | 1.849 | 1.849 | 1.846 | 1.843 | 1.843 | 1.84 | 1.842 | 1.845 | 1.842 | 1.842 | 1.838 | 1.838 | 1.838 | 1.838 | 1.835 | 1.835 | 1.835 | 1.832 | 1.832 | 1.832 | 1.832 | 1.829 | 1.829 | 1.826 | 1.826 | 1.826 | 1.826 | 1.823 | 1.823 | 1.82 | 1.82 | 1.821 | 1.82 | 1.818 | 1.816 | 1.816 | 1.81 | 1.813 | 1.81 | 1.81 | 1.81 | 1.807 | 1.807 | 1.807 | 1.803 | 1.803 | 1.803 | 1.803 | 1.797 | 1.797 | 1.794 | 1.794 | 1.791 | 1.793 | 1.79 | 1.787 | 1.787 | 1.787 | 1.784 | 1.781 | 1.781
1.923 | 1.923 | 1.923 | 1.923 | 1.923 | 1.92 | 1.92 | 1.92 | 1.92 | 1.92 | 1.92 | 1.92 | 1.92 | 1.917 | 1.917 | 1.917 | 1.917 | 1.917 | 1.917 | 1.914 | 1.914 | 1.914 | 1.914 | 1.914 | 1.914 | 1.914 | 1.914 | 1.914 | 1.911 | 1.911 | 1.911 | 1.911 | 1.911 | 1.911 | 1.908 | 1.908 | 1.908 | 1.908 | 1.905 | 1.905 | 1.905 | 1.905 | 1.905 | 1.905 | 1.905 | 1.902 | 1.902 | 1.902 | 1.902 | 1.902 | 1.902 | 1.902 | 1.899 | 1.899 | 1.899 | 1.899 | 1.899 | 1.899 | 1.896 | 1.896 | 1.896 | 1.896 | 1.896 | 1.893 | 1.893 | 1.893 | 1.893 | 1.893 | 1.893 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.887 | 1.887 | 1.887 | 1.887 | 1.887 | 1.884 | 1.884 | 1.884 | 1.884 | 1.884 | 1.884 | 1.881 | 1.881 | 1.881 | 1.881 | 1.881 | 1.881 | 1.878 | 1.878 | 1.878 | 1.878 | 1.878 | 1.875 | 1.875 | 1.875 | 1.875 | 1.875 | 1.872 | 1.872 | 1.872 | 1.872 | 1.872 | 1.869 | 1.869 | 1.869 | 1.869 | 1.869 | 1.869 | 1.866 | 1.866 | 1.866 | 1.866 | 1.866 | 1.863 | 1.863 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.857 | 1.853 | 1.853 | 1.853 | 1.853 | 1.853 | 1.85 | 1.85 | 1.85 | 1.85 | 1.85 | 1.847 | 1.847 | 1.847 | 1.844 | 1.844 | 1.844 | 1.844 | 1.844 | 1.841 | 1.841 | 1.841 | 1.841 | 1.838 | 1.838 | 1.838 | 1.838 | 1.835 | 1.835 | 1.835 | 1.835 | 1.832 | 1.832 | 1.832 | 1.829 | 1.829 | 1.829 | 1.826 | 1.826 | 1.826 | 1.826 | 1.823 | 1.823 | 1.823 | 1.82 | 1.82 | 1.82 | 1.817 | 1.817 | 1.817 | 1.817 | 1.814 | 1.814 | 1.814 | 1.811
1.922 | 1.919 | 1.919 | 1.919 | 1.919 | 1.919 | 1.919 | 1.916 | 1.916 | 1.916 | 1.916 | 1.916 | 1.916 | 1.916 | 1.916 | 1.916 | 1.916 | 1.913 | 1.913 | 1.913 | 1.913 | 1.913 | 1.913 | 1.913 | 1.91 | 1.91 | 1.91 | 1.91 | 1.91 | 1.907 | 1.907 | 1.907 | 1.907 | 1.907 | 1.907 | 1.907 | 1.904 | 1.904 | 1.904 | 1.904 | 1.904 | 1.901 | 1.901 | 1.901 | 1.901 | 1.901 | 1.901 | 1.898 | 1.898 | 1.898 | 1.898 | 1.898 | 1.895 | 1.895 | 1.895 | 1.895 | 1.895 | 1.895 | 1.895 | 1.895 | 1.895 | 1.895 | 1.892 | 1.892 | 1.892 | 1.892 | 1.892 | 1.892 | 1.889 | 1.889 | 1.889 | 1.889 | 1.886 | 1.886 | 1.886 | 1.886 | 1.886 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.883 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.877 | 1.877 | 1.877 | 1.874 | 1.874 | 1.874 | 1.874 | 1.874 | 1.874 | 1.871 | 1.871 | 1.871 | 1.871 | 1.868 | 1.868 | 1.868 | 1.868 | 1.868 | 1.865 | 1.865 | 1.865 | 1.865 | 1.865 | 1.862 | 1.862 | 1.862 | 1.862 | 1.862 | 1.859 | 1.859 | 1.859 | 1.859 | 1.856 | 1.856 | 1.856 | 1.853 | 1.853 | 1.853 | 1.853 | 1.853 | 1.85 | 1.85 | 1.85 | 1.847 | 1.847 | 1.847 | 1.847 | 1.844 | 1.844 | 1.844 | 1.844 | 1.844 | 1.841 | 1.841 | 1.841 | 1.841 | 1.838 | 1.838 | 1.838 | 1.835 | 1.835 | 1.835 | 1.832 | 1.832 | 1.832 | 1.832 | 1.829 | 1.829 | 1.829 | 1.826 | 1.826 | 1.823 | 1.823 | 1.823 | 1.82 | 1.82 | 1.82 | 1.82 | 1.817 | 1.817 | 1.814 | 1.814 | 1.814 | 1.811 | 1.811 | 1.811 | 1.808 | 1.808 | 1.805 | 1.805 | 1.805 | 1.802 | 1.802 | 1.799 | 1.799 | 1.796 | 1.796
1.923 | 1.923 | 1.92 | 1.92 | 1.92 | 1.92 | 1.92 | 1.92 | 1.917 | 1.917 | 1.917 | 1.917 | 1.917 | 1.917 | 1.917 | 1.917 | 1.914 | 1.914 | 1.914 | 1.914 | 1.914 | 1.914 | 1.911 | 1.911 | 1.911 | 1.911 | 1.911 | 1.911 | 1.911 | 1.911 | 1.908 | 1.908 | 1.908 | 1.908 | 1.908 | 1.908 | 1.905 | 1.905 | 1.905 | 1.905 | 1.905 | 1.905 | 1.902 | 1.902 | 1.902 | 1.902 | 1.902 | 1.902 | 1.902 | 1.899 | 1.899 | 1.899 | 1.899 | 1.899 | 1.896 | 1.896 | 1.896 | 1.896 | 1.893 | 1.893 | 1.893 | 1.893 | 1.893 | 1.893 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.887 | 1.887 | 1.887 | 1.887 | 1.887 | 1.884 | 1.884 | 1.884 | 1.884 | 1.884 | 1.881 | 1.881 | 1.881 | 1.881 | 1.881 | 1.878 | 1.878 | 1.878 | 1.878 | 1.878 | 1.878 | 1.875 | 1.875 | 1.875 | 1.875 | 1.875 | 1.872 | 1.872 | 1.872 | 1.872 | 1.869 | 1.869 | 1.869 | 1.869 | 1.869 | 1.866 | 1.866 | 1.866 | 1.866 | 1.866 | 1.863 | 1.863 | 1.863 | 1.863 | 1.86 | 1.86 | 1.86 | 1.857 | 1.857 | 1.857 | 1.857 | 1.857 | 1.854 | 1.854 | 1.854 | 1.854 | 1.851 | 1.851 | 1.851 | 1.848 | 1.848 | 1.848 | 1.848 | 1.848 | 1.845 | 1.845 | 1.842 | 1.842 | 1.842 | 1.839 | 1.839 | 1.839 | 1.839 | 1.836 | 1.836 | 1.836 | 1.836 | 1.833 | 1.833 | 1.833 | 1.83 | 1.83 | 1.83 | 1.827 | 1.827 | 1.824 | 1.824 | 1.824 | 1.824 | 1.821 | 1.821 | 1.818 | 1.818 | 1.818 | 1.815 | 1.815 | 1.815 | 1.812 | 1.812 | 1.812 | 1.809 | 1.809 | 1.806 | 1.806 | 1.803 | 1.803 | 1.803 | 1.8 | 1.8 | 1.797 | 1.797 | 1.794 | 1.791 | 1.791 | 1.788 | 1.788

## Capacity Analysis Form
Monomer Num | Residual Cap(AH) | Actual Cap(AH) | Cap Percentage
#1 | 37.2673 | 453.843 | 114.9%
#2 | 42.3649 | 452.3976 | 114.5%
#3 | 37.2673 | 453.843 | 114.9%
#4 | 0 | 430.7524 | 109.1%
#5 | 11.4147 | 437.8051 | 110.8%
#6 | 30.6752 | 453.794 | 114.9%